## Slide 1: SHELL FORM TRANSFORMERS Moscow - November 2018

## Slide 2: Introduction to Shell Form
Lucien Gaulard and John Dixon Gibbs exhibited a 'secondary generator' in London in 1882 and sold the idea to Westinghouse (USA) who developed shell form technology transformers in the United States from early 20th century,
In the 50’s, Mitsubishi (Japan) and Jeumont-Schneider (France) (est. 1905) - former JST signed license agreements with Westinghouse Electric Corp. and began manufacturing shell-form transformers.
Other manufacturers followed (in USA, Belgium, Spain, China, Portugal …).

## Slide 3: Shell vs Core, what are the differences?
HV Winding
LV Winding
Magnetic circuit
HV Winding
LV Winding
Magnetic circuit
Shell type :
Magnetic circuit: rectangular, surrounds the phase.
Phase: also almost rectangular
Windings groups: coaxial and alternate
Core type :
-Phase: circular
- Windings: concentric.
They surround the core which section is circular
Shell type
Core type
?

## Slide 4: three phase: Shell vs Core
Shell type
Core type
Three-phase configuration

## Slide 5: Shell vs Core transition in single phase
Single phase core type with 2 windings per leg
Single phase core type with concentric windings
Single phase core-type with interleaved windings
Upright shell type
Laid-down shell-type

## Slide 6: Shell form: Core construction
The same width for all laminations
Simplicity of design
Easiness to cut laminations
Accuracy of stacking
Ex : 8 x 8 SLC cutting
The magnetic circuit is free flux type
Same laminations width in all yokes
Single phase
Three phase

## Slide 7: Shell form: Phase construction (1)
etc…
CTC
cable
« standard »
cable
Windings: all made with rectangular flat «pancake» coils
Insulation between pancakes : pressboard washers with spacers
Windings: coaxial. All coils go around the same magnetic circuit
Adding coils: does not modify the mean turn of the group
Phase: sum of all the groups , alternating HV and LV along the phase axis
Insulating pressboard with spacer
Pancake coil
Pancake coil

## Slide 8: Shell form: Phase construction (2)
The phase:
built,
dried
and oil impregnated

## Slide 9: Shell Form: Tank construction
Tank base
Magnetic shields
Magnetic shields

## Slide 10: Shell Form: Assembly (1)
LV groups
HV group
Wood wedgings:
- inserted between phase and base walls
Tank base reinforcements

## Slide 11: Shell Form: Assembly (2)
Magnetic circuit
T beam: support the magnetic core, and reinforce the base
Steel wedgings :
- inserted between phase and core
Magnetic shields
Phase
Magnetic shields

## Slide 12: Shell Form: General configuration
Springs to press the magnetic circuit
Cover
Connections
Wedgings of the phase
Form-fit tank
(very close to the active part)
Bushing

## Slide 13: as built Shell Form
Single phase transformer
Three phase transformer

## Slide 14: Impedances vs Winding arrangements
G = 2 (2 HiLo) with impedance Z
G = 4 (4 HiLo)  impedance = Z / 2
With the same main data (power, voltages …), the 4 HiLo transformer impedance is half the one of a 2 HiLo transformer
Easiness to match whatever specified impedance, even low, just by playing on the windings arrangement, possibility of three or four secondaries with specific impedances
The leakage flux circulates around one winding only. The lines have a radial direction
General formula :

## Slide 15: Shell Form: Short Circuit Withstand
Limited Axial Forces
Main short circuit forces are in the axial direction.
Radial forces: negligible due to the accurate alignment of magnetic centers between coils and between groups.
Note: When changing the winding arrangement from a 2 HiLo to a 4 HiLo, with the same impedance, the total electrodynamic forces on the winding are divided by 2
coil
Pressboard
spacer

## Slide 16: Dielectric withstand example: Full wave applied on HV line
HV
LV
LV
CS
L
CT
CT
CT
CT
L
CS
CT
U(x)
U
CT : capacitance to earth
CS : series capacitance
L : inductance
% of winding from line
% of applied voltage
=0
=10
The windings of a shell-form transformer have very favorable geometry for a good surge voltage distribution :
The surfaces of the coils are very large  high series capacitances Cs
The coils present their thin edges towards the magnetic circuit  low capacitances to earth CT
naturally low

## Slide 17: Shell Form: Thermal behavior
For all types of cooling (natural, forced) oil is always directed into the windings
The oil :
enters into the base,
is fully directed inside the windings
and then calories are evacuated by the coolers
All elementary coils are cooled on each side thanks to oil channels made by the spacers path on pressboard washers
The homogeneity of oil flow in each oil channel and the large surface of coils in contact with oil allow a very efficient cooling

## Slide 18: Shell Form: Transportation
Single phase shell form transformers can be shipped laid down
Smaller gauge (shipping height)

## Slide 19: Shell Form advantages
Compactness :
Rectangular geometry
Form-fit tank very close to the active part
Reduced volume of oil (reduced oil-pit volume as well)
Cooling efficiency :
Oil always directed into the phases
Large surface of coils for a better cooling
Coils cooled on each side
Easy adaptation to any type of cooling
Structural:
Reduction of short-circuit forces by playing on the number of Hi-Lo channels
Windings sustained by both magnetic and tank reinforcements
Looseness mastering by both axial and radial wedgings
Capacitances & Impedance :
Natural high series capacitances of windings due to large surface
Natural low capacitances to earth due to the small thickness of coils
Easiness to match whatever specified impedance

## Slide 20
JST transformateurs: Shell Form Single Phase GSU (NPP)
650*MVA 405/23 kV
EPR- Flamanville- France
360*MVA 400/24 kV
France
  * Continuous rating per phase Plus many Three Phase ANTs and ASTs (34, 96, 100MVA) from 70’s up 2016
NPP GSU since the 70’s for EDF Nuclear Power Plants, from the 900 MWe NPP up to the 1650 MWe EPR NPP
=> Over 120 units delivered to EDF NPP - 360/550/570/650 MVA*

## Slide 21: JST transformateurs: Export Nuclear experiences
  KKG - Switzerland 970 MWe
  Gösgen Nuclear Power Plant - commercial operation: November 1rst , 1979
  4 x 400 MVA (per phase) 24kV/409kV supplied in 2008
  Krško- Slovenia 730 MWe
  Krško Nuclear Power Plant - commercial operation: January 15th , 1983
  1 x 500 MVA 21/400kV supplied in 2000

## Slide 22
Headquarter & main plant
Industrial or commercial subsidiaries
Transformers for Train: expressed in units.
Other Power Transformers: expressed in cumulated delivered MVA

## Slide 23
Hydraulic model
Development of a CFD (Computational Fluid Dynamics) model and measurements on an equivalent mock-up to validate the hypothesis of the numerical calculations.
Simulation of the complete transformer using the same hypothesis.
R&D main topics
Plexiglas mock-up in progress
Mock- up

## Slide 24: Construction of an hydraulic model
This mock-up allows to check and match :
the oil flow at the lower part of a pressboard washer,
Inlets
Outlets
Inlets
Outlets
the oil flow upper part of a pressboard washer
R&D main topics

## Slide 25: Oil speed measurement by Particle Image Velocimetry (PIV)
Treatment signal station
Camera
Laser (reflects the particles circulation)
R&D main topics

## Slide 26: Thermal-hydraulic simulation of a shell type coil
Temperatures under spacers
R&D main topics

## Slide 27: Mastering Load Losses due to leakage flux
R&D main topics

## Slide 28: VVER 1000 Main Transformer typical characteristics
General characteristics:
Generator Step-Up transformer
Shell Type Transformer
417 MVA HV= 420/√3 kV - LV =24 kV
Connection diagram YNd11 (for three phase group)
De-energized tap changer HV neutral side +/-2x 2,5 %
HV Insulation level
  Um 420 / SI 1175 / LI 1425 / LIC 1550 / AC 630 kV
Cooling and Structural:
ODAF : 4 air coolers + 4 pumps
Impedance and Losses:
Ucc = 14,45 % +/- 7 % base 417 MVA
No Load Losses = 164 kW +/- 15 %
Load Losses = 770 kW +/- 15 %
Auxiliary losses = 75 kW +/- 15 %
LV Insulation level
  Um 24 / LI 150 / LIC 175 / AC 65 kV

## Slide 29
Any question?